SECTION 7

WATER SUPPLY SERVICES

Contents

701		SCOPE

702		GENERAL

703		ADEQUACY OF WATER SUPPLY

703.1		General

703.2		Source of Supply

703.3		Treatment Facilities

703.4		Design of Storage Facilities

704		INSTALLATION OF WATER SUPPLIES

704.1		General

704.2		Water Pressure

704.3		Gravity and Surge tanks

704.4		Backflow

704.5		Stop Valves and Drain taps

704.6		Supply Pipes to Individual fixtures

704.7		Distribution Pipes

Table		7-1 	Minimum Size of Water Supply Pipes to Individual Fixtures

Table		7-2 	Minimum Size of Water Distribution Pipes

705		PIPELINE SYSTEM

705.1		General

705.2		Excavation of Pipe Trenches

Table		7-3 	Minimum Depth of Cover to the Crown of the Pipe

Table		7-4 	Maximum Particle Size

705.3		Pipe Laying

705.4		Jointing of the Pipe

705.5		Anchoring of Pipes

705.6		Hydraulic Testing of Pipe Lines and Joints

705.7		Disinfection of the Pipe Line

705.8		Back filling of Trenches

705.9		Connection of Accessories

705.10		Colour Code

706		UTILIZATION OF POTABLE GROUND WATER

707		DOMESTIC WATER PUMPS

708		SAFETY DEVICES

SECTION 7

WATER SUPPLY SERVICES

701		SCOPE

This Section provides guidance to persons who are submitting development proposals to the Authority and outlines the requirements for the provisions of water supply services for these developments. It is recommended that persons wishing to construct developments for buildings used by the public or housing developments of more than 10 units contact the Environmental Health Division for advice on the appropriate regulations affecting such developments in addition to the requirement of this Section.

702		GENERAL

a)	The developer is responsible for providing an adequate and potable water supply to his development. This will include the provision, as may be necessary, of a source(s) of supply, treatment facilities, pipeline system and storage facilities.

b)	Developers shall be fully responsible for the design and construction of water supply and sewerage systems for their developments and shall satisfy the Authority that there is adequate provisions for the operation and maintenance of such systems.

c)	Developers should be aware that rainfall in some of the islands averages less than 30 inches per year and that there may be no public pipe borne water supply in or adjoining the development area.

d)	In areas where there is a centralised water supply adjacent to or in close proximity to the development, the developer will carry out such work as may be required by the Authority and by the water authorities for connection to his development.

e)	The provisions in this Code regarding submission of plans, payment of fees and approvals shall apply.

703 		ADEQUACY OF WATER SYSTEM

703.1		General

a)	The applicant is to include in his proposal complete arrangements for providing an adequate quantity and quality of water to meet fully the needs of his development. The per capita consumption rate assumed for design purposes must be approved by the Authority.

b)	Minimum daily potable water consumption rates are as follows:

Dwelling house		40 gallons/person/day

Hotels			150 gallons /room/day

Offices			8 gallons/employee/day

703.2		Source of supply

The source of supply must be established with the approval of the Authority as below:

a)	Every building shall be provided with a water supply system and storage facility to the approval of the Authority.

b)	Where a piped water supply is available, the design must provide for individual storage facilities of a minimum capacity of 40 imperial gallons for each person regularly occupying the building, or in the case of buildings of public occupancy such as churches or theatres or industrial buildings, storage facilities which in the opinion of the Authority are adequate.

c)	The Authority may permit private residences in Group E (Sub-section 301.6) which are wholly dependent on rain water catchment to install catchment and storage facilities which would provide on average less than the 40 gallons per person per day recommended.

d)	Where no piped water supply is provided to serve the development, or unless a desalination plant is, or will be installed, the design submitted with the application for buildings in Groups B (Institutional Buildings) and E (Residential Buildings) must provide for individual rain water storage to the extent of 10 imperial gallons for each square foot of roof surface, except that for multi-family dwellings the capacity of the tank must be based on a minimum storage of 4,000 gallons per bedroom.

e)	Sub-section 703.2 d) will not apply if:

(i)	the building is to be supplied with potable water by means of desalination of non-potable water or by any other means such as to avoid the occupants of the building needing to rely on water being supplied from any existing public well or borehole, public tank or cistern or to extract potable water from any lens or underground water; and

(ii)	adequate back up system fed from an alternative source or 3 days storage, whichever is greater, is provided against the possible break down of the primary supply. The back up system is required to be in full working order at all times.

f)	A fault or breakdown in the primary system referred to in e) shall be repaired without delay.

g)	Abstraction from a ground water source requires prior approval of the Authority. Full details are to be supplied of the proposed borehole to be established including the intended rate of abstraction and available information on the aquifer.

h)	Pumping levels in the borehole will not be allowed to fall below 1.0 feet above mean sea level and the rate of abstraction must take into account the water needs of other developments, proximity to potential source of pollution such as a sewage outfall, and the characteristics of the aquifer in which the borehole is located.

i)	Desalination plants must be designed and constructed with the approval of the Authority and of the Ministry of Health. Full details of the proposed plant must accompany the application.

The details must include:

	location of the source of raw water,

	analysis of the raw water,

	capacity of the plant,

	main features of the treatment process,

	method of disposing of the effluent and

	future arrangements for operation and maintenance

j)	Sea water can be used for flushing of toilets and other such uses, but the water system carrying sea water must be kept separate from the system carrying potable water.

k)	There shall be no cross connection between a potable supply and a non-potable supply.

703.3		Treatment Facilities

a)	The water supply must be treated as necessary and disinfected by chlorination or other approved process to ensure that the quality satisfies the Guidelines for Drinking Water Quality as published by the World Health Organization in 1984, or other acceptable standard guidelines that are approved in writing by the Ministry of Health.

b)	The treatment facilities shall be designed and constructed to the satisfaction of the Authority and the Chief Environmental Health Officer.

703.4		Design of Storage Facilities

a)	Unless exempted by the Authority, buildings in Occupancy Groups A (Public Buildings) and B (Institutional Buildings) should be provided with at least 3 days storage of treated water based on the consumption estimates given in Sub-sections 703.1 and 703.2. This is in addition to any storage provided at the source of a public water supply.

b)	The location and design of the storage facilities, (tanks or cisterns) must be approved by the Authority and the Chief Environmental Health Officer. The applicant should provide the Director with drawings and calculations showing that the storage facilities are adequate and that the structure can safely support the water in the facility.

704		INSTALLATION OF WATER SUPPLIES

704.1		General.

As far as possible all pipelines should be laid underground and in a manner as not to interfere with future development and other services.

704.2		Water Pressure

If the water pressure from the water supply source is insufficient to supply all fixtures continuously, the supply shall be supplemented by a gravity tank or a surge tank linked to an auxiliary pumping system.

704.3		Gravity and Surge Tanks

(a)	Gravity and surge tanks shall be equipped with over flow pipes not less than 4" below the supply point and not less than twice the diameter of the supply and discharging directly to outside the building line.

(b)	Supply pipes from storage tanks may not connect to any public water mains supply system.

704.4		Backflow

a)	The water distribution system shall be fully protected against backflow either by use of air gap fittings or where it is not possible to provide an air gap, by non return valves or other means approved by the Authority.

b)	The Authority shall require that the developers of all institutional buildings and other facilities used by the public install and maintain back flow devices complying with recognised standards acceptable to the Ministry of Health.

704.5		Stop Valves and Drain Taps

(a)	A screw stop valve shall be provided within 5'0" of the point of entry of the main supply pipe to the building and a drain tap shall be provided within 1'0" of this valve on the distribution side. Such valve shall be plainly labelled.

(b)	Stop valves shall be provided on the supply within 1'0" of the supply connection to all storage tanks and water heaters and on all branch distribution pipes from such storage tanks and water heaters and to isolate all sanitary fixtures in groups of not more than five fixtures.

704.6		Supply Pipes to Individual Fixtures

Table 7-1 shall determine the minimum size of water supply pipe to a sanitary fixture provided that no supply pipe shall be smaller than the connection to a fixture and this shall determine the minimum size of supply pipe to fixtures not listed in Table 7-1.

704.7		Distribution Pipes

Table 7-2 establishes the maximum fixture unit load permitted for a given size of water distribution pipe and shall be used to determine the minimum sizes of water distribution pipe provided that:

(a)	Individual fixture unit ratings shall be taken from the Table.

(b)	Where the incoming central water supply pressure regularly falls below 50 lb. per sq. in. the next large size of pipe shall be used.

(c)	Where flush valve operated water closets are installed the minimum size of the main incoming supply shall be 1-1/2"

(d)	No section of distribution pipe shall be smaller than the largest branch pipe taken from it.

(e)	Not more than three fixtures shall be supplied by one 1/2" cold water pipe.

Table 7-1

Minimum Size of Water Supply Pipes to Individual Fixtures

| Description | Size of Pipe (in) | Description | Size of Pipe (in) |
| --- | --- | --- | --- |
| Bath tub | 1/2 | Water closet (cistern operated) | 3/8 |
| Bidet | 1/2 | Laundry tub | 1/2 |
| Drinking fountain | 3/8 | Shower | 1/2 |
| Flushing sink (cistern operated) | 1/2 | Slop sink | 1/2 |
| Flushing sink (flush valve operated) | 1 | Urinal (cistern operated) | 3/8 |
| Hose connection (flush valve operated) | 1/2 | Urinal (flush valve operated) | 1 |
| Kitchen sink (domestic) | 1/2 | Water closet (flush valve operated) | 1 |
| Kitchen sink (commercial) | 3/4 | Water heater | 1/2 |
| Washing machine | 1/2 |  |  |

Table 7-2

Minimum Size of Water Distribution Pipes

| No. of fixture units served | Size of pipe (in) | No. of fixture units served | Size of pipe (in) |
| --- | --- | --- | --- |
| 1 - 10 | 1/2 | 76 - 150 | 1 -1/2 |
| 11 - 25 | 3/4 | 151 - 300 | 2 |
| 26 - 50 | 1 | 301 - 600 | 1-1/2 |
| 51 - 75 | 1-1/4 | 101 - 1,200 | 3 |

705		PIPELINE SYSTEM

705.1		General

The pipeline system must be designed and constructed to the satisfaction of the Authority.

705.2		Excavation of Pipe Trenches

(a)	The centre line of the pipe trench should be within the right of way but not under the road surface. The width of the trench should be 18 inches minimum and otherwise the minimum width required to enable the work to be done but not less than 12 inches greater than the diameter of the pipe. The depth of the trench should be such as to provide the minimum cover over the crown of the pipe under any carriage way measured from finished road surface as shown in Table 7-3.

Table No. 7-3

Minimum Depth of Cover to the Crown of the Pipe

| Pipe Diameter | Depth of Cover (ft-in) |
| --- | --- |
| Up to 6" | 2-6 |
| Over 6" and up to 10" | 2-9 |
| Over 10" and up to 20" | 3-0 |

(b)	The trench should be excavated in straight lines between changes in direction and be carefully graded so that there is a minimum number of substantially high points along its length.  Air valves are to be installed at high points in the line subject to prior approval of the location and size of the air valve in each case. Where the trench has been excavated too deep, it shall be filled to grade with thoroughly rammed approved granular material, subject to paragraph (c) below.

(c)	Subject to para. (e) below a 4 inch depth of the bottom of the trench should be of selected material having no particle larger than that indicated in Table 7-4 for pipelines of the material as shown in the Table.

(d)	In peaty or boggy ground the bottom of the trench should be excavated to an approved depth below grade and refilled with broken stone, and a bedding of chips should be laid over the broken stone and thoroughly rammed to grade.

(e)	In rocky ground the bottom of the trench should be filled to a depth of 6" with material no larger than that given in Table 7-4.

Table 7-4

Maximum Particle Size

| Pipe material | Maximum particle size of selected material (in) |
| --- | --- |
| Grey Cast Iron or Ductile Iron | 1 |
| Steel or Copper | 3/4 |
| PVC | 1/4 |

705.3		Pipe Laying

a)	Pipes must be laid in straight lines between  changes in direction. The entire length of the barrel of the pipe must be supported on the bottom of the trench.  Care must be taken to ensure that the inner surface of each pipe is left clean after laying.  When pipe laying is not in progress the ends of the pipeline should be plugged to prevent ingress of foreign matter.

b)	Pipes laid under high ground water conditions must be plugged and backfilled between joints before testing so as to avoid floating of pipelines. The location of pipes must be marked.

c)	Pipes laid under drains, water courses, channels, concrete slabs, culverts, or other conduits should be laid in a sleeve extending at least two feet on each side of the conduit, beyond the side wall of the conduit or toe of embankment supporting the conduit. The sleeve may be of steel or ductile iron pipe or other material approved by the Authority and be surrounded in concrete if the cover to the pipe is less than 18 inches or provided with such other protection as maybe required by the Authority.

705.4		Jointing of the Pipe

The developer must conform to the manufacturers' instructions as regards the procedure for proper laying and jointing of the particular type of pipe and joint being used in the development. Other basic requirements for a satisfactory joint are:

a)	Cleanliness of all parts

b)	Correct location of components

c) 	Centralization of spigot and socket sleeve.

d)	True alignment in vertical and horizontal planes.

705.5		Anchoring of Pipes

a)	Thrust blocks must be provided at tees, crosses, dead ends and at all bends (except concave vertical bends).  In the case of bends, the blocks should be located symmetrically with the pipe fitting which should be symmetrical with the radial centre line.  The thrust blocks should be constructed of 2,500 lb. concrete, reinforced if required, and must rest firmly on the solid ground.

b)	The required area of bearing on the solid earth will vary with the type of soil, and the area of bearing on the pipe fitting must be sufficient to safely transmit the thrust through the block. Information on the soil bearing and shear capacity must be submitted with the request for design approval.

c)	Pipelines of PVC or other flexible materials must use thrust blocks as required by the manufacturers' specifications.

705.6		Hydraulic Testing of Pipe Lines and Joints

a)	After all work in connection with the laying of the pipeline system has been completed, the developer shall issue to the Authority a certificate of final inspection and testing. The testing shall be carried out by qualified engineers or technicians approved by the Authority.

b)	The developer shall be responsible for meeting the cost and carrying out the testing of the pipeline system as required by the Authority and as set out hereunder.

c)	Air vents must be provided at the upper end of the section of pipeline to be tested and at other locations as required.  The line should be slowly filled, preferably from the lower end. The pressure should be increased to 150 percent of the anticipated working pressure and be sustained for 2 hours.

d)	The pipeline and joints will be accepted as  having satisfied the test if the leakage does not exceed 1 gallon per inch of pipe diameter per mile of pipeline for each 100 feet to test pressure. The measure of leakage is the volume of water required to be pumped into the pipeline so as to re-establish the test pressure.

705.7		Disinfection of the Pipe line

a)	Newly installed pipe lines must be flushed and the water tested before being put into use. The developer must provide and fix a valve of the same diameter as the pipeline in a suitable location for the effective flushing of the line.

b)	After the pipe line has been flushed it shall then be charged with water to which has been added chlorine at the rate of 50 parts per million parts of water.  After 24 hours the pipe line will be thoroughly flushed after which samples will be collected and tested by a reputable laboratory approved by the Chief Environmental Health Officer. The testing regime shall be to the approval of the Ministry of Health.

c)	If the laboratory examination shows that the pipe line has not been adequately disinfected, the disinfection shall be repeated until satisfactory samples have been obtained.

c)	All tests are to be carried out at the expense of the developer and to the approval of the Chief Environmental Health Officer.

705.8		Back filling of Trenches

Selected material should be firmly tamped by hand rammers around and to a height of 12 inches above the top of the pipe. Natural excavated material should then be tamped by hand rammers to a height of 24 inches over the top of the pipe, thereafter the remainder of the backfill composed of natural excavated material may be tamped by mechanical tamper.

705.9		Connection of Accessories

a)	Methods for connecting water pipes and fittings of dissimilar materials are subject to approval by the Authority.

b)	The methods of connecting to the pipeline such accessories as service or communication pipes, hydrants, sluice valves and air valves are to be approved by the Authority. Particular attention should be paid to the material to be used and method to be employed in backfilling the trench or supporting the accessory.

c)	Service or communication pipes of 1/2", 3/4" and 1" diameter may be either of copper equivalent to ANSI B 16.22-1980 or PVC Schedule 40 or as approved by the Authority. The pipe shall be laid to a minimum depth of 18" below the surface of the carriage way and terminate on the pavement (sidewalk), the end of the pipe being securely plugged pending final connection into the premises to supplied with water. The backfill material should be thoroughly tamped by hand rammers.

d)	In new developments fire hydrants must be provided at locations as required by the Authority. In areas where fire engines cannot reach the building, dry mains must be provided. Cisterns should also be made accessible to fire hoses, if necessary by constructing a special basin outside of the cistern for receiving a fire hose.

e)	Air valves shall be either single or double orifice type as may be required. They shall be fitted with a lock test pressure of 400 feet head of water without leakage.

705.10		Colour Code

Where water supply pipelines and sewers are laid in close proximity to each other a colour code or other means of identification must be adopted, with the approval of the Authority, to ensure that each can be readily identified.

706 		UTILIZATION OF POTABLE GROUND WATER

(a)	Fresh ground water utilization shall normally be limited to government approved developments except where the Authority considers that a particular case merits special consideration.

(b)	No restriction shall be imposed on fresh ground water use in individual dwelling plots if the method of extraction is limited to hand pumps or buckets. However the wells must be properly sealed to the approval of the Environmental Health Department, to prevent contamination of the well water.

(c)	Unless otherwise approved by the Authority, pumping of any well shall not cause depression of the water level.

(d)	A well for potable water supply shall penetrate the fresh water zone only to a maximum of one third of the depth of the fresh water lens.

(e)	Wells shall be provided with surface aprons to a distance of five feet around the well, and the well-tops shall project above the surface apron to a minimum height of two feet, and be equipped with a sanitary well seal, all to be constructed of approved materials, to ensure that no direct entry of any surface water can occur through the well.

(f)	Wells shall be located a minimum of the indicated distances away from sources of pollution, as follows:

(i)	Pit latrines, septic tank and sewers:150 ft.

(ii)	Cesspools:				150 ft

707 		DOMESTIC WATER PUMPS

a)	Where a water pump is provided as part of a private domestic water supply it shall be sized to maintain a minimum of 20 lbs. pressure under all conditions of water use. A pressure tank of adequate capacity shall be installed. It is recommended that the plumbing within 3 ft. of the water pump be of galvanised steel to prevent melting of the plastic pipe fittings if the pump should run dry.

b)	Paper and charcoal filters placed in the domestic water supply line will help in reducing colour and odour in the water supply. However, no reliance shall be placed on passive filters to remove disease organisms from contaminated water.

708 		SAFETY DEVICES

a)	A pressure relief valve shall be installed for all equipment used for heating or storing hot water. Hot water shall be run in copper or CPVC pipe. Regular PVC pipe shall not be used.

b)	Water hammer is caused by loosely fixed pipes, bends or taps such as self-closing or spring type which shut off too quickly. It is more likely to occur in long branches than when the tap is fixed close to the supply line. An air vessel or dead-end riser pipe shall be fixed as close to the pipe as possible in order to absorb the shock and thus minimize water hammer.