SECTION G

FIRE PREVENTION AND FIRE SAFETY

Contents

1.	SCOPE

2.	FIRE RESISTANCE CONSTRUCTION

2.1	General Requirements

3.	RECOMMENDATIONS

4.	FIRE RESISTANCE RATING OF MATERIALS OF CONSTRUCTION

Table	E-1	Minimum thickness of concrete walls

Table	E-2	Minimum cover to main reinforcement of

reinforced concrete beams

Table 	E-3	Minimum sizes of concrete columns

Table 	E-4	Fire resistance time assigned to wall board

members

Table 	E-5	Rated fire resistance period for concrete block walls and partitions made of limestone aggregate and plastered both faces.

Table 	E-6	Minimum finished thickness of walls for various fire ratings

SECTION G

FIRE PREVENTION AND FIRE SAFETY

1.	SCOPE

This Section provides general guidelines for fire resistance construction of small buildings used generally for domestic purposes and for small retail and storage facilities not exceeding 2,500 square feet in area. This Section however, does not cover construction requirements for storage or retail facilities of flammable or hazardous material as defined in the Building Code.

Section 4 of the Building Code gives more detailed information of the fire resistance construction requirements of materials used in construction. Developers are advised to consult the Code for the design and construction of any building which may be outside of the scope of these Guidelines.

2.	FIRE RESISTANCE CONSTRUCTION

2.1	General Requirements.

a)	Fire safety within the scope of these guidelines would require the following:

i)	Direct access of occupants to the outside from the kitchen and at least one other room.

ii)	Use of a non-flammable material in the construction of exposed components. For example, some types of synthetic material used for ceilings and light partitions are flammable, and some drapery material is considered to be very vulnerable and dangerous.

b)	Domestic fires would generally start in the kitchen areas from malfunctioning stoves, or from burning firewood or coals dropping on timber floors.  Electrical fires are not common, but must be considered seriously as more houses are now being electrified and bad wiring and overloaded circuits can produce dangerous situations in timber houses.

c)	Fire safety depends not on the use of appropriate materials but on safe construction practices, and on safe use of household appliances.  The structural sizes used for masonry buildings within the scope of these Guidelines are adequate for  hour fire resistance, but lightweight partitions and ceilings of fibreboard or plaster board will provide only 10 to 30 minutes of resistance to fire.

d)	Timber buildings are, as expected, very vulnerable.  The fire resistance of  inch fibreboard is 5 minutes, and that of 5/8 inch Douglas fir plywood which is preferred sheathing, is 15 minutes.  Timber studs and joists in a properly constructed building have resistance of 10 to 20 minutes.

3.	RECOMMENDATIONS

3.1	It is recommended therefore that the following steps be taken to prevent and to limit the spread of fires in a small building:

a)	Interior partitions constructed of either timber or concrete block should be carried to the underside of the roof.

b)	Ceilings should not be made of flammable material.

c)	Drapes, curtains, cushion coverings etc. made of synthetic materials should not be in kitchen areas.

d)	Kitchens should have an exterior door which opens outwards.

e)	All exterior doors of the house should open outwards, but interior doors may open inwards.

f)	All windows should be capable of being opened from inside the house.  Hurricane shutters should be removed as soon as possible after an emergency is over.

g)	Stairways should be at least 3 feet wide to make it possible for injured persons to be carried down the stairs to safety.

h)	Kitchen floors should be concrete and if of timber, should be covered with a fire resistant material.  Stoves should not be placed near material which is not fire resistant.  If this is necessary, protecting the timber with zinc or aluminium sheeting is recommended, as this would inhibit the start of fires.

i)	Inspection of all electrical installations should be rigorously pursued in accordance with relevant Electricity Regulations in force.

j)	Steel frames should be encased in concrete at least 1- inch thick, as steel structures fail suddenly under extreme heat.

3.2	It is recommended that designers and builders of large buildings outside the scope of these Guidelines seek guidance from the Building Code or from relevant Code such as the Caribbean Uniform Building Code (CUBiC), in addition to consulting the Fire Services Department.

4.	FIRE RESISTANCE RATING

a)	The Tables which follow give the fire rating of various materials of construction commonly used in small buildings. The  designer and builder must recognise that the fire resistance  quoted are for sound materials used properly. It is the responsibility of the designer to ensure that the building is constructed in a manner that would limit the spread of a fire and that the occupants would be able to escape through the doors or ground floor windows. (For more information on fire prevention see Appendix H of the Building Code)

b)	Table G-6 gives the fire resistance of partitions and walls constructed of solid concrete (limestone aggregate) with horizontal reinforcement not less than 0.25% and vertical reinforcement of not less than 0.15% .

TABLE G-1.

Minimum thickness (in.) of concrete walls.

| Concrete type | Minimum slab thickness for fire rating of: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 hr | 1-1/2 hr. | 2 hr. | 3 hr. | 4 hr |
| Portland cement with limestone aggregate | 3.2" | 4.0" | 4.6" | 5.7" | 6.6" |
| Light-weight aggregate | 2.5" | 3.1" | 3.6" | 4.4" | 5.1" |

TABLE G-2.

Minimum cover to main reinforcement of

reinforced concrete beams (unrestrained.)

| Beam Width (ins) | Cover thickness (ins) for fire resistance rating: |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 hr. | 2 hr. | 3 hr. | 4 hr. |
| 5 | ¾ | 1-1/4 | - | - |
| 7 | ¾ | ¾ | 1-3/4 | 3 |
| 10 | ¾ | ¾ | 1 | 1-3/4 |

Note: 	The covers recommended in Section D. paragraph 2.4 c) would provide a fire resistance of about 4 hours for lintel and beams if constructed as recommended.

TABLE G-3.

Minimum sizes of concrete columns.

(least dimension required for structural stability)

| Type of Construction | Minimum column dimension (ins) for fire resistance rating. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Reinforced concrete (limestone aggregate) | 4 | 8 | 12 | 16 |
| Concrete block (cavities filled) | 8 | 8 | 12 | 16 |

Note:	Column sizes recommended for single story concrete block  building will provide a 1  hr.

TABLE G-4.

Fire resistance time assigned to wall board members

| Description of finish. | Time in minutes. |
| --- | --- |
| 1/2" fibreboard | 5 |
| 3/8" Douglas fir | 5 |
| 5/8" Douglas fir | 15 |
| 3/8" Gypsum wallboard | 10 |
| 5/8" gypsum wallboard | 30 |
| Double 3/8" gypsum wallboard | 25 |

Note:	Partitions made of fibreboard or plywood must be well constructed to provide the fire resistance quoted. However it is recommended that fibreboard not be used for exterior siding.

TABLE G-5.

Rated fire resistive period for concrete block walls and partitions made of limestone aggregate and plastered both faces.

| Construction | Min. finished thickness face to face (ins) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 hr. | 2 hr. | 3 hr. | 4 hr. |
| Cavities filled | 3 | 4 | 6 | 6 |
| Cavities hollow | 8 | - | - | - |

Note:	The fire resistance of hollow concrete block depends on the quality of the block and the quality and thickness of the plaster covering. Hollow concrete blocks unplastered would not achieve a one hour rating.

Table G-6

Minimum finished thickness (ins) of walls and partitions for various fire ratings.

(solid reinforced concrete walls)

| Ratings | 1 hr. | 2 hr. | 3 hr. | 4 hr. |
| --- | --- | --- | --- | --- |
| Wall thickness | 3-1/2 | 5 | 6 | 6-1/2 |