SECTION H

PLUMBING, SANITATION, WATER SUPPLY AND GAS INSTALLATIONS

Contents

1.	GENERAL REQUIREMENTS

1.1	Prohibited fittings and connections

1.2	Dead ends

1.3	Changes in direction

1.4	Supports and hangers

2.	SOIL AND WASTE SYSTEMS

2.1	Pipe materials

2.2	Pipe sizes

2.3	Workmanship

2.4	Gradients and self-cleaning velocities

2.5	Joints and connections

2.6	Plumbing fixtures

2.6.1	General

2.6.2	Water Closets

2.6.3	Flushing cisterns

2.6.4	Lavatory basins/sinks

2.6.5	Shower baths

2.6.6	Drinking Fountains

2.6.7	Traps

2.6.8	Water Seals

2.6.9	Clean outs

2.6.10	Venting systems

2.6.11	Manholes/Inspection chambers

2.6.12	Trenches

2.6.13	Pipes under floors and walls

2.6.14	Toilet flushing ball valves

2.6.15	Electrolytic action

3.	SANITATION

3.1	Sanitary drainage

3.2	Single pipe system

3.3	Dual pipe system

3.4	Setting out drainage works

4.	SEPTIC TANKS

4.1	General

4.2	Location

4.3	Construction

4.4	Operation

4.5	Maintenance

5.	GREASE TRAPS

6.	SUBSURFACE DISPOSAL

6.1	Percolation tests

TABLE 	H-1	Percolation Tests

6.2	Tile fields

6.3	Location and setbacks

6.4	Soakaway

6.5	Disposal wells

6.6	Percolation criteria

6.7	Size requirements for soakaways

TABLE 	H-2	Size Requirements for Soakaways

6.8	Construction

6.9	Location

TABLE 	H-3 	Approximate Dimensions of Septic Tanks

7.	"PACKAGE PLANTS"

8.	COMPOST PRIVIES

9.	PIT PRIVIES

9.1	Location

9.2	Construction

9.3	Maintenance

10.	CESSPOOLS

10.1	General

- SURFACE WATER DISPOSAL

  - General requirements

- SOLID WASTE DISPOSAL

12.1	General Requirements

13.	WATER SUPPLY

13.1	Workmanship

13.2	Capacities of pipes

TABLE  H-4	Size and Number of Branches

13.3	Cross Connections

13.4	Water supply equipment

13.4.1	Reverse osmosis water makers

13.4.2	Water heaters

13.4.3	Domestic water pumps

13.5	Safety devices

13.6	Toilet flushing ball valves

14.	WATER STORAGE CISTERNS

14.1	General

14.2	Location

14.3	Construction

14.4	Operation

15.	ARRANGEMENTS FOR DISABLED PERSONS

16. 	GAS INSTALLATIONS

16.1	General

16.2	Cylinders

16.3	Pipework

TABLE 	H-5	Pipe Sizes for Individual Appliances

16.4	Appliances

16.5	Flueing and Ventilation

16.6	Testing

Figures

H-1	Schematic Drawing Showing Connection of Fixtures for a Single Storey Building

H-2	Detail of manhole Construction

H-3	Conventional Privy

H-4	Details of Construction of Water Cistern

H-5        Standard Septic Tank Details

H-6        Alternative Arrangements of Sanitary Fixtures in a Bathroom

H-7        Soak-aways in Areas with High Water Table

H-8        Soak-aways in Areas with a Low Water Table

SECTION H

PLUMBING, SANITATION AND WATER SUPPLY

1.	GENERAL REQUIREMENTS

1.1	Prohibited fittings and connections

No soil or waste pipe shall be fitted with double hubs, double tees or double y's (without an access door).

No waste water pipe shall discharge into a bend attached to a water closet bowl.

Fig. 21 illustrates the acceptable connections of lavatory fixtures for a single storey dwelling.

1.2	Dead ends

Wherever a dead end exists or is proposed for a soil or waste system, it shall be laid so as to prevent any accumulation of waste.

All unconnected openings in a drainage system with the exception of a vent pipe shall be properly capped so as to be both air and water tight.

1.3	Changes in direction

All horizontal changes in direction of soil or waste pipes shall be provided with an accessible inspection chamber or clean-out.

22  degree bends and sanitary tees may be used for changes in direction of flow from horizontal to vertical.

Bends, tees, y's and crosses may be used to effect changes in direction in vent and water distribution pipes.

1.4	Supports and hangers

All vertical piping shall be supported, anchored and adequately fixed with spacings not exceeding 5 feet and not exceeding 3 feet at offsets or branch connections. All horizontal piping shall be supported, anchored and adequately fixed to prevent sagging at each hub, for cast iron and copper, at 6 foot intervals, and throughout its length for pitch fibre and PVC.

Pipe hangers shall be fixed to stone, brickwork, blockwork or concrete by means of expansion-type plugs. Hangers of copper shall be of the same material as the pipe or if of different material be insulated to prevent electrolysis.

Drains laid in unstable ground shall be supported on a layer of 1:3:6 concrete not less than 4 inches thick and 6 inches on either side wider than the pipe diameter.

2.	SOIL AND WASTE SYSTEMS

2.1	Pipe materials

Generally these shall be of suitable material, hard, smooth, impervious and non-corrosive, such as copper, PVC, or cast iron.

Black iron, galvanized iron or concrete pipes are not recommended for use as soil pipes.

2.2	Pipe sizes

The diameter of pipes shall be as small as may be consistent with the maximum load, but soil pipes shall not be less than 3 inches in diameter.

Waste water pipes shall not be less than 1 " in diameter.

2.3	Workmanship

All plumbing shall be installed in a workmanlike manner.

After laying, soil and ventilating pipes shall be capable of withstanding smoke or air tests under pressure, have no bends (except where unavoidable) in which case bends shall be as obtuse as possible so as not to reduce the internal diameter of the pipe.

Soil/waste pipes shall discharge so as not to cause dampness to any foundation or wall of a building.

The building sewer line and the potable water line shall not be laid in the same trench and the possibility of cross connection shall be avoided. (see Sub-section 11.3)

2.4	Gradients and self-cleansing velocities

Soil pipes shall be laid at a minimum gradient of 1:40 for 4 inch pipes and 1:60 for 6 inch pipes.

Waste pipes carrying some solids shall be laid at a minimum gradient of 1:30.

Self cleansing velocities would be achieved if velocities are approximately 2.5 feet per second with the pipe flowing  full.

Drain field pipes shall be laid at a gradient of 1:200

2.5	Joints and Connections

All joints and connections shall be of the same material and shall be air and water tight.  They shall be so constructed as to allow the free flow of waste and, before commissioning, be swabbed and cleaned inside to avoid obstructions of the bore.

In joining soil pipes the spigot or grooved end of the pipe shall be laid in the direction of flow or downstream.

Joints to soil pipes shall be as follows:

(a)	for lead - wiped or burned

(b)	for cast iron - sockets made with hemp or yarn and metallic lead properly caulked

(c)	for pitch fibre - tapered couplings

(d)	for PVC - with a suitable fitting and sealed and welded with solvent cement.

(e)	for vitrified clay/salt glazed ware sockets made with tarred hemp or gasket and the remaining space filled with 1:3 cement: sand mixture.  It is a mistake to use neat cement as the cement will shrink on setting, resulting in a leaky joint.

f)	No coating or painting shall be applied before testing.

g)	Where waste pipes are connected to soil pipes all pipes are to be constructed in the same way as specified for soil pipes.

2.6	Plumbing Fixtures

2.6.1	General

Generally these shall be of smooth, hard, durable, impervious and corrosion-resistant materials free from flaws and blemishes.

2.6.2	Water closets

Water closet bowls shall be of vitreous china, vitreous glazed earthenware or other suitable material.

Water closet bowls shall be attached to the floor and/or wall with a normal height of 16 inches above floor level and be fitted with a seat of smooth non-absorbent material.

"Low water use" water closets are available from various manufactures and should be used wherever water consumption is a consideration, such as from a cistern supply.

The use of a separate saltwater well flushing system will greatly reduce the use of fresh water from the cistern.  All components of the salt water system shall be plastic.  The salt water will not interfere with septic tank operation.

2.6.3	Flushing cisterns

Water closet flushing cisterns shall have a capacity of not less than 2 imperial (2.4. U.S.) gallons. They shall have flush valves which are easily accessible for repairs and flush pipes of not less than 1  inches in diameter.  When low level cisterns are used, larger flush pipes are necessary.  Flushing cisterns are normally used only in commercial settings. Pressure flow toilets may also be used with 1/4 gallon flush closets.

2.6.4	Lavatory basins/sinks

The top front edge of every lavatory, basin or sink shall be fixed at a normal height of 36" above the finished floor level with waste pipes of not less than 1  inches for sinks and 1  inches in diameter for basins.

Fixtures for special uses, such as in lavatories to be used by handicapped persons or by children, shall be mounted at the appropriate heights for the applications.

Every lavatory basin or sink shall be provided with an overflow, connected on the building or inlet side of the trap.

2.6.5	Shower baths

Shower and tub outlets shall not be less than 1  inches in diameter and be fitted with removable strainers.  The use of "water saver" shower heads is encouraged.

2.6.6	Drinking fountains

Drinking fountains shall have orifices located above the highest overflow level of the receptacle and be shielded so that the drinker cannot put his lips on the orifice.

2.6.7	Traps

Traps forming an integral part of plumbing fixtures shall be supplied with the fittings to which they are to be attached.  Those intended to disconnect from the drain or wastes are placed at the foot of wastes from lavatory basins, sinks, baths and drinking fountains.  They are generally S or P traps. S traps are not recommended because they lose their seal easily.

All fixtures connected to foul drainage shall be trapped as close to the fixture as possible.

No trap with partitions shall be used and crown venting off the upper curve of an "S" trap is not permitted as this results in accumulations in the vent.

2.6.8	Water seals

All traps shall have a minimum water seal of 3 inches for soil and 2 inches for wastes and be not less than 3 inches diameter for soil fixtures and 1  inches for waste water.

2.6.9	Clean-outs

Every clean-out shall be equal thickness to the wall thickness of the pipe, be readily accessible, shall open opposite to the direction of flow or at right angles to it and shall provide adequate space for cleaning.

2.6.10	Venting systems

All water closets shall have a vent pipe of not less than 2 inches in diameter.

Vent pipes shall also be used when two or more waste fittings are connected into a soil or waste pipe.  See Figure 21. They shall be connected above floor level rim of the highest fixture served and so graded to drip back to the soil or waste pipe.

Vent pipes shall be extended to a minimum distance of 1 foot above the roof of any habitable room or to a greater distance as may be prescribed by the authority for unusual situations such as roof gardens. Screens shall be installed on the top of the pipe for mosquito control.

Flashings at vent terminals shall be water tight and shall preferably be fitted with a wire cage so as to permit the free passage of air.

It is essential that a drain be ventilated to prevent the accumulation of foul air and to maintain equal pressure inside and outside the system.  It is better to have a vertical vent pipe at the head of the drainage system, carried up to a height at which it is unlikely to cause a nuisance, and to omit an intercepting trap at the sewer near to the property boundary.  This enables the sewer as well as the individual drainage system to be ventilated.

Soil and soil ventilating pipes may be used to provide this ventilation if they occur in suitable positions.

2.6.11	Manholes/Inspection Chambers

Manholes/inspection chambers shall be installed at every change of direction and gradient and on straight runs be spaced no more than 40 feet apart to allow for easy rodding and cleaning.

Manholes shall be constructed of reinforced concrete or concrete blockwork, and the drain, where it passes through the manhole, shall be carried in an open channel. Channels shall be adequately benched, glazed, and be constructed of impervious material.

Branches are connected to the drain at manholes and their invert levels shall be above the main invert to prevent fouling at the mouth of an unused branch.

The widths and lengths of excavation for manholes will depend on requirements; the length being determined by the number of branches or by the depth.  Manholes below the surface of the ground to a depth of 2 ft shall be a minimum size of 2' long by 1 ' wide.  Those between 2 ft and 4 ft deep shall be a minimum of 3 ft long by 2 ft wide.

Manhole covers shall be of reinforced concrete steel or similar durable material and shall be airtight and fitted with lifting handles to facilitate removal.

2.6.12	Trenches

Trenches for laying of building sewers shall not be less than 18 inches wide.

Care shall be taken to back fill and ram them carefully in layers not exceeding 6 inches deep in order that the drain may not be injured or broken.  It is good practice to water the trench during the back-filling process to assist in consolidating the returned material.  It is desirable to arrange for the best material to be returned to the trench when back-filling, leaving the rubbish to be carted away.

2.6.13	Pipes under floors and walls.

No part of a drain shall be laid under a building unless absolutely necessary.

Where a drain is laid under a floor, not being a suspended floor, it shall be laid in a straight line for its entire length beneath the building. But in no case shall the drain under the building be longer than 40 feet.

Where drains are laid on piers, they shall be placed on sound foundations and shall be a minimum size of 10" by 10" and be spaced not more than eight feet apart.

Rodding and flushing eyes shall be easily accessible, shall open opposite to the direction of flow, and shall provide adequate space for rodding and flushing.

2.6.14	Toilet flushing ball-valves

Where a ball-valve is used, a relief pipe shall be provided in the silencing pipe immediately below the valve outlet to avoid siphonage.

The rating of ball valves shall be checked with the manufacturer's data. If a low pressure valve is installed on a high pressure system, dribbling will occur thereby wasting water and increasing the consumer's bill in a metered water supply.

2.6.15	Electrolytic action

Dissimilar metals shall not be connected because of the danger of electrolytic (galvanic) action with resulting corrosion.

3.	SANITATION

3.1	Sanitary Drainage

The type of drainage to be adopted will depend upon the facilities for disposal of waste matter.

3.2	Single pipe system

In sewered areas, all waste shall be discharged through the soil pipe or building sewer to the sewerage system.

In areas where there is no sewerage system and where sub-surface drainage is adequate, all waste shall preferably be discharged into septic tanks or other approved installations employing the water carriage system.

3.3	Dual pipe system

In areas where sub-surface disposal is inadequate, soil and waste shall preferably discharge separately;  soil pipe to the septic tank and waste pipe to a soakaway, surface drain, or garden. Waste water from the kitchen should preferably be directed to the soakaway pit via a ell designed grease trap.

In either system, branch drains shall be a short as possible.

3.4	Setting out drainage work

The lines of drains can be set out by driving stakes along one side of the proposed trench and stretching a line tightly between them.

The trenches can then be excavated to the required depth and gradient.  The most accurate and labour-saving method of excavating to required gradients is by means of "sight rails" and "boning rods".  A sight rail is a horizontal rail secured to two uprights braced one on either side of the trench and a boning rod is a long T square.

Timbering the side of trenches shall be effected for deep trenches in treacherous ground in order to prevent accidents.

Where the excavation is greater than  5 feet deep, and except in rock, the sides of every excavation in connection with building operations, including trenches for pipes or for any purposes, shall be sheet-piled, braced or shored when necessary to prevent the soil from caving in on persons engaged in work within such excavation. The work shall be done to the satisfaction of the Senior Planning Officer, but the responsibility for safety of the work lies with the builder.  In such circumstances consultation with an engineer is advised.

4.	SEPTIC TANKS

4.1	General

- The Public Health (Sewage and Disposal of Sewage and Industrial Waste Works) Regulations SRO 218 provides information on size, location, construction, operation, and maintenance of septic tank systems. Septic tank systems must be designed, located, constructed, used and maintained to the satisfaction of the Chief Environmental Health Officer (CEHO).

b)	The basic function of a septic tank is to receive domestic sewage, partially treat it, segregate the solids, and discharge the liquid to a tile field or soakaway. Anaerobic bacterial action breaks down much of the solid matter into liquids and gases.  While in an efficiently operating tank the liquid discharge is comparatively clear, tanks do not accomplish a high degree of bacteria removal and infectious agents including pathogenic organisms may be widespread in the effluent which is "septic."

c)	The primary purpose of the tank is to condition sewage during which time the following functions take place:

i)	Removal of solids in the following approximate quantities: 100% settleable solids and 70% suspended.  The heavier solids settle to the bottom forming a blanket of sludge and the lighter ones rise to the surface to form a scum layer.

ii)	Decomposition by anaerobic bacterial and natural processes -  the organic strength being reduced by approximately 30%.

iii)	Storage of sludge and scum so that the sludge and other material accumulated between cleanings will not be scoured into the disposal field and clog the system.

d)	Septic tanks shall not be undersized or be constructed in series, as the velocity of flow through two identical tanks is the same as the velocity of flow through one of them.  This type of arrangement virtually doubles the velocity and results in the carry over of 70% suspended material.  The heavier solids settle to the bottom forming a blanket of sludge and the lighter ones rises to the surface to form a scum layer.

f)	It is recommended that all designers of septic tanks consult the Environmental Health  Department to ensure that the system design and capacity are acceptable.

4.2	Location

a)	Tanks shall be located not less than 10 feet from any dwelling. The Public Health Regulations stipulate that septic tanks shall not be less than 50 feet from any well or drinking water source and 100 feet from high water mark.

b)	Tanks shall be located where the largest possible area is available for the disposal arrangements.

4.3	Construction

a)	Two compartment tanks achieve better clarity of effluent than single compartment tanks.

b)	Tanks shall preferably be constructed of reinforced concrete block work rendered on the inside and base, or of 1:2:4 reinforced concrete.  Provide removable cover slabs or manholes over inlets and outlets and an air space of 12 inches.

c)	Inlets and outlets shall be so located as to avoid disturbance of surface scum.

d)	The approximate dimensions and construction of a septic tank for a single family home shall be as follows:

i)	Walls

6" reinforced concrete with 1/2" dia. bars at 8" vertically and 1/2" dia. bars at 16" horizontally, or

8" concrete block filled with 1:3:6 concrete and with ladder type reinforcement every other course. The inside face to be plastered with two courses of 3/8" cement mortar.

ii)	Top and Bottom Slabs

6" reinforced concrete with 1/2" dia. bars at 12" centres longitudinally.

Slope of bottom slab to 1/4" to 1'0".

iii)	Access Hatches

Access Hatches to be patented cast iron or steel covers 18" or 2'0" square, or of 4" thick concrete with 4" mesh reinforcement.

- Information on minimum septic tank dimensions can also be obtained from the  Environmental Health Department– and Table H-1

TABLE H-1

MINIMUM SEPTIC TANK DIMENSIONS AS RECOMMENDED

BY THE ENVIRONMENTAL HEALTH DEPARTMENT,

MINISTRY OF HEALTH

| Max No. Of Pers. | Bed Rooms | Sludge Chamber | Effluent Chamber | Width | Liquid Depth | Air Space | Vol. Gallon |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 - 4 | 1 – 2 | 4’ 0” | 2’ 0” | 3’ 0” | 4’ 6” | 1’ | 500 |
| 6 | 3 | 6’ 0” | 2’ 0” | 4’ 0” | 4’ 6” | 1’ | 900 |
| 8 | 4 | 7’ 6” | 2’ 6” | 4’ 0” | 4’ 6” | 1’ | 1115 |
| 10 | 5 | 9’ 6” | 3’ 0” | 4’ 0” | 4’ 6” | 1’ | 1395 |

Note: For flow rates greater than 1395 gallons per day consult the Department.

4.4	Operation

a)	Sludge has been found to accumulate at the approximate rate of 0.92 cu.ft./person per year and scum at the rate of 0.42 cu.ft./person per year.

b)	Tanks should be cleaned when the level of the bottom of the scum is within 3 inches or the surface of the sludge is within 18 inches of the bottom of the outlet fitting (tie or bend).

c)	Only small quantities of soap and detergents normally used in the homes should be discharged to the tank.  Large doses of chemicals such as bleach will kill or inhibit bacteria.

d)	Water from roofs, weeping tiles, or foundation drains and surface run-off shall be excluded as large volumes of clear water will stir up the contents, reduce the retention time and carry solids to the disposal field.

e)	Bacterial action can be started off by seeding with animal manure.

f)	Paper towels, newspapers, wrapping paper and rags should not be used as they will not decompose in the tank.

4.5	Maintenance

a)	Tanks should be inspected every year with a view to cleaning probably in 3 years.

b)	A chart should be prepared for each building showing the location of tank and disposal system.  It should contain brief instructions for inspection and maintenance, thus forestalling failures.

b)	Tanks shall not be entered until they are thoroughly ventilated and gases removed in order to prevent accidents from explosions or asphyxiation.

5.	GREASE TRAPS

Approved septic tanks are of sufficient capacity to allow for greases normally discharged from houses.

Where, in the opinion of the CEHO, there is to be an excessive discharge of grease/oil, such as a restaurant kitchen, a grease/oil trap shall be installed.

Traps shall be designed for 2.5 US gallons capacity per person with a minimum capacity of 125 gallons.

6.	SUBSURFACE DISPOSAL

a)	Suitability of a soil for a subsurface disposal system is dependant on its percolation rate and this is generally determined by the Environmental Health Department or by a percolation test.

b)	Soil texture can be used, with certain limitations, as a means of determining absorption capabilities and preliminary indications shall be obtained by examination of roads cuts, stream embankments and excavations for foundations.  The larger the particles, the larger the fines and the faster will be the percolation rate.  If the soil appears to be suitable, percolation tests shall be made.  This method is an acceptable and reliable means of obtaining soil absorption capabilities.

6.1	 Percolation tests

The procedure is summarized as follows:

(a)	Dig three holes 1 ft. x 1 ft. to a depth of approximately 2  ft. in the area of the proposed drain field or soakaway.

(b)	Remove all loose material.

(c)	Add 6 inches of fine gravel to protect the bottom from scouring or sediment.

(d)   	Fill with clean water and saturate overnight.

(e)	Fill the holes with clean water again the next day and time how long it takes in minutes for the water level to drop 1".

(f)	Consult Table H-2 below to find required size of tile drainage field.

g)	Use the average of the times for the three holes.  If it takes longer than 60 minutes for the water to fall, the area is not suitable for a drain field, and another area or method of disposal must be used.

h)	If the house includes a garbage disposal unit, add 25% to the above trench figures.

TABLE H-2

Percolation Tests

| Time to fall 1 inch (mins) | Sq. ft. of trench per bedroom |
| --- | --- |
| 2 or less minutes 3 4 | 75 85 95 |
| 5 6 - 10 11 - 15 | 105 135 160 |
| 16 - 30 31 - 45 46 - 60 | 205 245 275 |

6.2	Tile fields

A tile field removes pollution by means of percolation through the soil in which there is bacterial action.

6.3	Location and Setbacks of Tile Fields

a)	Tile fields shall not be less than 100 ft. from an underground water supply, 50 ft. from a creek, canal, lake, or coastline and 10 feet from a dwelling house or property line.

b)	Tile fields shall not be less than 4 ft. above the ground water table and when located in rocky areas require a 50 ft. apron of earth sufficient in depth to promote bacterial growth.  They may be raised or partly raised to achieve those conditions.

c)	Tile fields shall be located away from tree roots.  Heavy machinery shall be excluded from the disposal area and whenever possible sufficient space for an additional field shall be allowed should the original field fail or become clogged. Tile fields shall be tested and inspected before back filling.

d)	Tile fields are constructed by digging trenches, placing gravel at the bottom the trenches, laying the perforated pipe or open joint tile in a gentle gradient from the distribution box, covering with tar paper, and backfilling.  The trenches are generally 18" wide by 24" deep with 6" of gravel on the bottom.  Bends and other fittings should be kept to a minimum in the drain field.

6.4	Soakaways

Soakaways shall be used as alternatives to shallow absorption fields where sub-surface conditions are feasible. They shall never be used where there is likelihood of contaminating underground water supplies, such as areas with fresh water wells.

The most suitable disposal system is dependant on the percolation rate and this is generally determined by the Environmental Health Department.

6.5	Disposal Wells

Disposal wells must not be used in any fresh water lens area without the express permission of the CEHO.

6.6	Percolation criteria

a)	Soils with absorption rates of less than 1" in 30 minutes are unsuitable for soakaways.

b)	Capacity of soakaways shall be computed on the basis of percolation tests (as above) made in each stratum penetrated.

c)	Absorption area required shall be based on the effective vertical wall area.  No allowance shall be made for the bottom or area above the inlet.

6.7	Size Requirements for Soakaways

a)	Table H-3 shows the size of soakaway required for various soil conditions. Add 25% to the areas for houses with garbage disposals.

b)	For example a three bedroom house on a site with a percolation rate of ten minutes for a drop of one inch, the soakaway pit would have to be about 8 ft. by 6 ft. by 8 ft. deep. For a percolation rate of two minutes or less the pit can be 6 ft. by 4 ft. by 6 ft. deep.  For a rate of 30 minutes it is suggested that two pits be constructed, each 8ft. by 6ft. by 8ft. deep.

TABLE H-3

Size Requirements for Soakaways

| Time for water to drop 1" | Area of pit walls per bedroom (sq.ft.) |
| --- | --- |
| 2 mins or less 3 4 | 40 50 55 |
| 5 10 15 30 | 60 75 90 150 |

c)	It is important however that a test be carried out at each building site, as soil types vary widely and the size of the pit depends on the type of soil.  The Chief Environmental Health Officer may require a developer to increase the size of a soakaway if he deems it necessary.

6.8	Construction

a)	In the construction of soakaways proper precautions shall be taken to prevent the side walls from collapsing while workmen are in the hole.

b)	The soakaway pit is to be lined with stones, bricks, or concrete blocks laid up dry with open joints backed up with at least 3" of gravel.  The bottom of the pit is to be filled with coarse gravel (pea rock), to depth of at least one foot.  The cover is to be made of reinforced concrete.

6.9	Location

a)	The criteria for location of soakaways is similar to that for tile fields.  Where two soakaways are to be constructed they shall be located not less than three times the largest of the surface dimensions apart.

b)	The area selected for construction shall be large enough to allow for additional pits should there be failure.

c)	Soakaways may be used in all areas for the disposal of excess rainwater or runoff from buildings that is not of a septic nature.

7.	"PACKAGE PLANTS"

Proprietary aerobic sewage treatment plants are available for small dwellings and/or buildings.  They shall be considered either for larger buildings or groups of buildings where it is not possible to build a proper septic tank/leach field system. There must be an adequate provision of skilled personnel for their operation and maintenance and be designed and constructed in accordance with the Public Health regulations  and to the satisfaction of the Chief  Environmental Health Officer.

.

The water recovered from these systems is often suitable for irrigation use after proper post treatment.

Sewage treatment plants shall not be purchased or installed without the prior approval of the Chief Environmental Health Officer.

8.	COMPOST PRIVIES

Compost privies have been successful only where there has been a high degree of user care and attention.  They are still in the evaluation phase and should be carefully investigated before steps are taken to construct them.

9.	PIT PRIVIES

9.1	Location

a)	Pit privies shall be sited in accordance with Public Health regulations and to the satisfaction of the Chief Environmental Health Officer .

b)	They shall preferably be located on the leeward side of a building or as otherwise approved by the Environmental Health Department.  In densely populated areas, pit privies may not be allowed.  Privies shall be ventilated.

c)	Privies shall not be used in areas where the water table is within 2 feet of the surface since they will not function well.  They will be odorous and the contents will not compact.  Raised pit latrines could be used in areas of high water table.

d)	Where a pit privy is impracticable, consideration should be given to alternative means of disposal in consultation with the Environmental Health Department.

9.2	Construction

a)	The precast concrete slab pit privy has been adopted by many health authorities.

b)	There shall be openings at the top of the walls to dissipate odours and, in case of the Ventilated Improved Pit Latrine  to provide the through draft required for functioning of the vent pipe.

c)	The door should open outwards in order to minimize the internal floor area.

d)	The toilet shall be sufficiently screened to discourage flies.

e)	The walls and roof shall be weatherproof, shall provide privacy, exclude vermin and be architecturally compatible in external appearance with the main house.

f)	Seat height shall be 16 inches above the slab level and the size of the seat opening 10 inches in diameter.  To encourage proper use by children and to prevent their falling into the pit, a second smaller 6.0 inches diameter seat should be provided.  This may be a separate seat on the seat cover.

g)	For maximum odour control in the latrine, the vent pipe shall be at least 6.0 inches in diameter, painted black, screened with a wire gauze and located on the sunny side of the latrine so that air inside the pipe will heat up and create an updraft.

h)	The size of the pit should not be greater than 4' 0" by 4' 0" and at a depth of about 6' 0".

i)	Figure H-4 shows a typical arrangement of a pit privy with a precast concrete box on a concrete slab.

9.3	Maintenance

If water enters the pit, a cupful of kerosene can be poured into  it at weekly intervals to control mosquito breeding.  If the seat  cover is replaced in the horizontal position after use, this will  also help in mosquito control.

10	CESSPOOLS

10.1	General

Cesspools are watertight underground sewage storage chambers sometimes used in rural districts and are usually emptied at regular intervals by a special vehicle which transports the sewage to a disposal point.

Cesspools are ordinarily not permitted.

Where cesspools have been allowed by the Environmental Health Department they must be:

(a)	Watertight.

(b)	Properly covered.

(c)	So sited as to permit easy access for emptying under all weather conditions.

(d)	Of a depth not exceeding 14 feet (4.3 m) below the cover in order to allow the suction hose of the emptying truck to be used.

If odours occur they can be controlled by the use of lime.

No disinfectants shall be used in the pit.

- SURFACE WATER

  - General

- Consideration must be given to surface water drainage on the site.

- Roof and other surface water pipes or drains must discharge in an existing drainage channel or in a soakaway built specifically for that purpose.

- Surface water should not be disposed on adjoining lands without the consent of the owner.

- Provisions for surface water drainage shall be to the satisfaction of the Ministry of Communications and Works.

- SOLID WASTE DISPOSAL

  - General Requirements

(a)	Consideration must be given to the collection and disposal of solid waste during construction and occupation of a building.

- Solid waste, including excess fill, rubble and debris from construction sites should be disposed at designated sites only and the disposal must be carried out in occordance with the rules and regulations of the Environmental Health Department.

( c )	Bins should be provided for the storage of refuse.  Such bins must be properly constructed to prevent entry by rodents.

13.	WATER SUPPLY

13.1	Workmanship

All water supply pipes shall be installed in a workmanlike manner and be provided with a properly protected and easily accessible stop cock or gate valve near to the boundary of the plot or at the water pump location. The work shall be carried out to the satisfaction of the CEHO and the Water and Sewerage Authority where connections are being made to the public water supply.

13.2	Capacities of pipes

TABLE F-3 gives the numbers and sizes of smaller diameter branch or distribution pipes that may be taken off a supply pipe (or rising main), which are to be all in service at the same time.

# TABLE H-3

Size and Number of Branches

| Size of pipe or riser main | 1-1/4" | 1" | 3/4" | 5/8" | 1/2" |
| --- | --- | --- | --- | --- | --- |
| 1-1/4" | 1 | 2 | 4 | 6 | 10 |
| 3/4" | - | - | 1 | 2 | 3 |
| 1/2" | - | - | - | - | 1 |

Many more branches are generally taken off based on the assumption that water will be drawn intermittently and only a percentage of the branches are used at any one time.

The minimum size of a branch or distribution line shall be  inches (13 mm).

13.3	Cross connections

The building sewer and potable water pipes shall not be laid in the same trench.

Sewer lines shall be laid at a lower elevation and in any case with inverts not less than 12 in. below the invert of the water service pipe and horizontally as far apart as practicable.  Vertical separating distances shall be increased at crossover points.

There shall be a break or gap between the inlet levels and the top water levels in receptacles where the inlet level is below the surface e.g. in swimming pools, bidets and some flushing cisterns and washing machines.

Direct connections of pipes and valves between public and private water supplies are not allowed, even on a stand-by basis.  Irrigation lines and soaker hoses can be a source of cross connections. They must be designed to avoid siphonage of dirty water back into the supply line through the use of vacuum breakers and anti-syphon valves.  Professional advice shall be sought for these situations.

Close attention shall be given to avoiding possible back siphonage of dirty water from toilets, lavatory basins etc. into the water supply pipes or by direct connection between waste and water pipes.

13.4	Water Supply Equipment

13.4.1	Reverse osmosis water makers

Reverse osmosis water makers are complex machines that can be used to remove salt and other minerals from sea or brackish water. They can be used to provide a source of potable water in a location that has no other water resources.  Because of the operational and maintenance requirements of these units, they should be installed and operated by skilled professional personnel.

13.4.2	Water heaters

Water heaters may be obtained for gas, electric, solar, or oil fuel.  Solar heaters are recommended for economy of operation and energy conservation.

Solar heaters are of two types, gravity convection feed and pumped.  The gravity operated units need less maintenance, but require the solar panels to be mounted below the tank.

Solar water heaters can be supplied with booster elements to maintain water temperature on cloudy days or at night.

Professional advice should be sought for the position and mounting of solar water heaters.

13.4.3	Domestic water pumps

Where a water pump is provided as part of a private domestic water supply, it shall be sized to maintain a minimum of 15 lbs. pressure under all conditions of water use.  The pump is usually set for 30 lbs. cut-in and fifty pounds cut out.  A pressure tank of adequate capacity shall be installed.

It is recommended that the plumbing within 3 feet of the water pump be of galvanized steel to prevent melting of plastic pipe fittings if the pump should run dry.  Special pressure switches are available to shut off the pump if the supply runs dry.

Paper and charcoal filters placed in the domestic water supply line will help in reducing colour and odour in the water supply.  However, no passive filter will remove disease organisms from contaminated water.

13.5	Safety devices

A pressure-relief valve must be installed for all equipment used for heating or storing hot water.  It opens automatically against the adjustable setting of the spring.

The size of hot-water piping installations can be one size smaller than cold-water ones.   Hot water must be run in copper or CPVC pipe.  Do not use regular (white) PVC.   A check valve placed in the cold water supply line to the conventional (not solar) water heater will save energy by stopping convection circulation.

Water hammer is caused by loosely fixed pipes, use of sharp bends, or taps such as self-closing or spring types which shut off the supply quickly.  It is more likely to occur in long branches than when the tap is fixed close to the supply pipe.  An air vessel or dead end riser pipe shall be fixed as close to the tap as possible in order to absorb the shock and thus minimize water hammer.

13.6	Toilet flushing ball valves

Where a ball-valve is used, a relief pipe shall be provided in the silencing pipe immediately below the valve outlet to avoid siphonage.

The rating of ball valves shall be checked with the manufacturer's data. If a low pressure valve is installed on a high pressure system, dribbling will occur thereby wasting water and increasing the consumer's bill in a metered water supply.

14.	WATER STORAGE CISTERNS (Fig. H-4)

14.1	General

In areas without a public water supply, a water storage cistern should be constructed for each house or dwelling, along with a rainwater collection system from the roof or other suitable catchment.

14.2	Location

The water storage cistern can be located under one or more buildings of a dwelling group or consist of a separate tank remotely located.  The cistern shall be located uphill and as far as practical from any septic tank, privy, soakaway, or leaching tile field.

14.3	Construction

a)	The water storage cistern shall be of reinforced concrete, concrete block, treated timber with a suitable liner, treated metal, or reinforced plastic construction.  It shall be sized and constructed to comply with the Building Code but should have no less than 10 gallons capacity for each square foot of roof or catchment area.

b)	The coating or liner in the water storage cistern shall be of a material that is approved for contact with potable water if the cistern is to be used for domestic drinking or cooking water.

c)	The cistern shall be provided with an access hatch to allow cleaning  out and repairs.

d)	The cover of the water storage cistern shall be of a durable, non-rotting material. Wood or plywood is generally not satisfactory. The cover must be tightly fitting to prevent mosquito breeding. Light should be excluded from the cistern water to prevent the growth of algae.

e)	Sufficient overflows must be provided to prevent flooding of dwellings. The overflows must be screened to prevent the entrance of mosquitos, frogs, or vermin.

f)	The catchment can consist of the dwelling roof area or a specially constructed concreted or lined area to capture rainwater. PVC guttering and downspouts is recommended for roof catchments.

g)	If the water is to be used for domestic drinking and cooking purposes, the catchment area must be protected from contamination by animal and human activity.  Hillside catchments should be fenced off and accessible deck areas or roofs separately drained to soakaways to prevent dirt, manure, etc., from being washed into the storage tank.  Catchments must not be coated with any paint that contains harmful substances.

h)	The use of asbestos roofing tiles for catchments is no longer acceptable and constitutes a major health risk.

i)	Do not coat catchment roofs with any paint  containing lead compounds.

14.4	Operation

It is a good practice to sanitize the water in the cistern by the addition of two teaspoons of bleach per 100 gallons of water if contamination is suspected.  If no bleach is available, the water should be boiled before drinking.

The cistern and its catchment should be cleaned on a regular basis and scrubbed with a sanitizing bleach solution if it is to be used for drinking water.

15.	ARRANGEMENTS FOR PERSONS With DISABILITY

Appendix F of the Building Code and Appendix A of  - Accessibility Guidelines for Persons with disability - of these Guidelines  provides information on the layout of access to sanitary facilities and to other public areas for persons with disability.  Designers of small public buildings such as retail shops, which may fall within the scope of the Guidelines, should consult  the Appendices, the other references noted  and the Grenada National Council of the Disabled to ensure that appropriate access arrangements are made for disabled persons.

16.	GAS INSTALLATIONS

16.1	General

a)	Propane gas installations for domestic size cookers, instantaneous water heaters, and storage water heaters shall comply with the following requirements. For other appliances, installations shall be in accordance with BS 5482.

b)	The standard operating pressure for propane is 37 mbar (14.8" w.g.). Regulators and appliances will normally have been set and designed for this pressure, but this should be checked through local suppliers of the product.

c)	Internal installations must be totally gas tight. There is no acceptable level of leakage.

d)	Gas installations should be undertaken by persons with appropriate experience.

16.2	Cylinders

Cylinders must be positioned upright on a level concrete hard standing outside the building, in well ventilated conditions. There must be no opening into the building within 3' 0" of the cylinders, and the tops of the cylinders, regulators and manifolds must be 1' 0" below the bottom window line.  When these requirement cannot be met the Fire Services of the Royal Grenada Police Force should be consulted

16.3	Pipework

a)	Pipework shall be one of the following:

i)	Annealed or half hard copper pipe to BS 2871: Part 1 Table X or W, or Schedule 40 copper pressure pipe with screwed taper threaded fittings to BS 143.

ii)	Medium weight galvanised screwed steel pipe to BS 1387 or Schedule 40 galvanised pressure pipe with screwed taper threaded fittings to BS 143.

b)	For compression fittings, only plain parallel soft copper olives should be used. Shaped brass or hard copper olives are not  acceptable. Particular care should be taken to follow the manufacturer's recommendations on tightening, and to ensure that the joint is gas tight.

c)	Screwed joints must be carefully made to ensure gas tightness. Pipe threads should be carefully cut, preferably with the use of a block die rather than adjustable die stocks. Never use two parallel threads together. The male thread must be tapered and sealed with PTFE tape. Do not use other general purpose jointing materials. Do not use a long thread connector and back nut; mechanical unions should be used where there is a need to be able to disconnect appliances or to break into pipework.

d)	The following pipe sizes given in TABLE H-5  are recommended for final connections to individual appliances. For longer runs or combined runs, consult pressure loss and pipe flow charts.

TABLE H-5

Recommended Pipe Sizes for Individual Appliances

| Appliance | Pipe size for up to 10' 0" run | Pipe size for 10' 0" to 20' 0" run |
| --- | --- | --- |
| Single point instantaneous water heater | 10 mm (3/8") | 15 mm (1/2") |
| Cookers, multi- point instantaneous water heaters and storage heaters. | 15 mm (1/2") | 22 mm (3/4") |

e)	Pipework should be properly clipped and supported against surfaces or may be buried in concrete or screeds. Where buried, it must be protected against corrosion. Where pipes run through block walls, they must be unjoined and sleeved and must pass through without running into open cores parallel to the walls. Sleeves should be sealed with flexible sealant to allow movement. If it is desired to run the pipework in the block cores then the pipe and fittings must be protected against corrosion and the cores solidly filled with concrete.

16.4	Appliances

a)	Unless, it is room-sealed, no gas appliance shall be installed in a bathroom, shower room or completely enclosed garage, such as those with solid doors.

b)	Propane gas is heavier than air and tends to accumulate at low points where it can create an explosion hazard. Appliances and cylinders shall therefore not normally be sited in basements or other areas from which the gas could not readily disperse. The siting of the appliance must be approved by the satisfaction of the Fire Services Department.

c)	Appliances should be sited so as to minimise the likelihood of pilot lights being extinguished by draughts. Before choosing the positions of the appliance, the intended location of the flue should also be considered.

d)	The final connection to the appliance may be in copper or steel and must include a union or compression fitting for easy disconnection. Each connection point must be provided with a service valve close to the appliance, so that it can be isolated and removed without shutting down the whole system. Fitting a permanent plugged pressure test point at the inlet of the valve will facilitate pressure and leak testing.

e)	Valves must be designed for use with propane. Ordinary gate valves are not suitable. Some taper plug taps (mitre cocks) are suitable as long as they are of the spring-loaded type. Propane dissolves oil and oil based lubricants, so  a special lubricant such as Rocol MT-LM Grease should be used. Saunders screw-down diaphragm type  valves with neoprene diaphragms may be used. Ball valves with PTFE inserts needing no lubricant may also be used - e.g. Orseal, Ballafix or Copass.

f)	Correctly made soft copper olive type compression joints give a perfect seal that can be broken and remade.

16.5	Flueing and Ventilation

a)	For cookers and single point instantaneous water heaters, no special flueing and ventilation requirements apply, provided that the rooms in which they are installed are not tightly sealed during use.

b)	Other appliances should be installed so as to ensure an adequate supply of air for combustion and adequate venting of the combustion gases. The manufacturer's recommendations should be observed.

c)	Generally, sufficient air for ventilation will be provided by normal doors and louvred windows, provided that no draught-seals are used. The installer should advise the householder not to close windows or louvres completely during use.

d)	If the appliance is installed in a location with ample permanent openings such as a garage or utility room with fixed louvres, special flueing arrangements may not be required. Draughty  locations which may extinguish the pilot light should be avoided. Where such conditions do not apply, a flue will be required. Balanced flues, which draw air from and discharge combustion gases to the exterior of the building, should be installed in accordance with the manufacturer's  recommendation. Open flues, which do not draw air directly from the exterior, still require the appliance to be sited with sufficient ventilation air as described in the previous paragraph. Open flues should be as short and vertical as possible, with no right angle bends, and should be sleeved where they pass through combustible materials such as timber boarded roofs. The manufacturer's recommendations should be observed.

16.6	Testing

a)	Propane gas installations must be absolutely gas tight and must be  pressure tested with a manometer or U gauge for leakage, pressure drop and burner pressure.

b)	The leak test is best carried out before making the final connection to the appliance(s). The procedure is as follows:

i)	Turn off the appliance isolating valves.

ii)	Fit a pressure test nozzle to the outlet of one isolating valve.

iii)	Attach the tubing from the U gauge to the pressure test nozzle.

iv)	To pressurize the system turn on the gas supply at the cylinder.

v)	Slowly turn on the isolating valve to which the U gauge is attached. (A sudden opening of this valve may cause a surge of pressure and blow the water out of the U gauge).

vi)	Turn off the service valve or cylinder valve firmly to ensure that no further supply of gas can enter the system.

vii)	Note the U gauge reading. It should be about 37 mbar (approx 15" w.g.). If it is obviously dropping there is a considerable leak somewhere which must be found and stopped before proceeding further.

viii)	Slowly release some pressure from the system so that the U gauge reads about 30 mbar (12" w.g.). This ensures that any locked up high pressure gas between the gas supply valve and the inlet to the regulator is expanded to low pressure, and also makes sure that gas is not recharging the system through a faulty supply valve which has not been totally closed. A supply valve letting gas into the system could compensate for a leak of gas out of the system so that the leak is not detected.

ix)	Leave for five minutes to allow the gas temperature to equalize with the temperature of the pipework.

x)	After five minutes note the precise reading of the U gauge.

xi)	Leave for a further five minutes and then check the U gauge reading again. There will be no pressure drop if the installation is sound. If the level of the water in the U gauge has fallen, there is leak somewhere. The speed at which the level falls gives an indication of the size of the leak. If the level of water in the U gauge has risen, the gas supply valve is letting gas by, and the leak test is not valid.

c)	This test may alternatively be carried out by pressurizing the system with air, and using a bicycle pump connected via a tee, with a tap to disconnect the pump after pressurizing.

d)	If the installation is sound, turn off the valve to which the U gauge is attached and remove the U gauge. Attach a length of tubing to the test nozzle, long enough to reach outside the building to as safe place. Turn on the supply and open the isolating valve to purge air from the line. Continue until you  can smell gas, then turn off the  valve. Do not attempt to ignite it.

e)	Make the final connection to the equipment and turn on the isolating valve(s). Check the appliance connection for leaks using soap solution brushed all over joints. Look for air bubbles appearing, which would indicate leaking connections.

f)	The pressure drop test procedure is as follows:

i)	Connect the U gauge to the manufacturer's pressure point on the inlet pipe to the appliance. This is located before the appliance control taps. If there is no manufacturer's test point, fit a temporary tee piece in the inlet pipe. Turn on the supply.

ii)	Note the U gauge reading. This shows the static pressure in the service with no gas flowing.

iii)	Light the pilot and note the U gauge reading. This may show a slight drop as gas starts flowing.

iv)	Operate all the appliances at full gas rate and note the U gauge reading. This shows the dynamic pressure with the gas flowing at maximum rate. The pressure drop between the pilot gas rate and the maximum gas rate should not exceed 2.5 mbar (1"). Drops greater than this probably indicate a partial blockage, or pipework which is undersized.

g)	Many appliances have a series of controls in the gas supply built in between the inlet and the burner, which present a restriction to the gas flow and cause a pressure drop, so that the burner is operating at a pressure lower than the inlet pressure. The manufacturer will quote the burner pressure and fit a test point at the burner so that this pressure may also be checked. The burner pressure test procedure is as follows:

i)	Turn the appliance control taps to the "off" position.

ii)	Slacken or remove the screw in the pressure test point.

iii)	Attach the tubing from the U gauge to the test point.

iv)	Turn the appliance control taps and operate the appliance at maximum rate.

v)	Note the U gauge reading. This should correspond with the manufacturer's information. Assuming that the line pressure at full gas rate was satisfactory, any substantial difference between the U gauge reading and the figure given by the manufacturer points to a fault in the appliance controls.