SECTION 3

GENERAL REQUIREMENTS

Contents

301		GROUP CLASSIFICATION BY USE AND OCCUPANCY

301.1		Basis of Classification

301.2		Group A	Public Buildings

301.3		Group B	Institutional Buildings

301.4		Group C	Commercial and Industrial Buildings

301.5		Group D	Office, Administrative and Retail Service Buildings

301.6		Group E	Residential Buildings

301.7		Group F	Hazardous Occupancy Buildings

302		OCCUPANCY CONTENT OF A BUILDING

302.1		Basis of Calculation

Table     	3-1	Occupancy Content of a Building

303		TYPE CLASSIFICATION BY CONSTRUCTION

303.1		Abbreviations

303.2		Basis of Classification

304		PERMISSIBLE AREAS AND HEIGHTS

304.1		Abbreviations

304.2		Basis of Determination

305		FIRE RESISTANCE RATINGS FOR BUILDINGS

305.1		Basis of Determination

306		SPECIAL PROVISIONS

306.1		Interpretation

306.2		General Occupancy

306.3		Hazardous Occupancy

306.4		Areas, Heights and Volumes

306.5		Special Fire Resistance Ratings

Table		3-2 	Type Classification by Construction

Table		3-3	Permissible Areas and Heights

Table		3-4	Fire Resistance Ratings for Buildings within 10'0 of Site Boundaries

Table 		3-5	Fire Resistance Ratings of Buildings between 10'0" and 20'0" of Site Boundaries

Table 		3-6	Fire Resistance Ratings of Buildings over 20'0" from Site Boundaries and more than 35'0" High.

Table 		3-7	Fire Resistance Ratings for Buildings over 20' from Site Boundaries and up to 35'0" high

SECTION 3

GENERAL REQUIREMENTS

301		GROUP CLASSIFICATION BY USE AND OCCUPANCY

301.1		Basis of Classification

Certificates of use and occupancy shall be based on the following group classification subject to the special provisions of 306 of this Code and provided that:

(a)	Any building having a use or occupancy not specifically mentioned shall be classified in the group it most nearly resembles.

(b)	Different buildings on the same property shall be certified separately for use and occupancy even when constructed under one permit.

(c)	Adjoining parts of the same building may be certified separately for different use and occupancy provided the division between them satisfies the fire resistance requirements of this Code for the most restrictive use.

(d)	More than one use and occupancy shall be permitted in any building without division provided the building conforms to the requirements of this Code for the most restrictive use.

301.2		Group A  Public Buildings

Being buildings in which 50 or more persons regularly congregate for civic, educational, religious, social or recreational purposes and including:

Assembly halls

Auditoria

Cinemas

City and town halls

Clubs, excluding residential accommodation

Court-houses

Dance halls

Permanent exhibition buildings

Games buildings

Lecture halls

Passenger assembly buildings

Public baths

Public art galleries, libraries and museums

Restaurants seating 50 or more persons

Religious buildings of all types

Teaching facilities of all types

Theatres

301.3		Group B. Institutional Buildings

Being buildings in which inmates' liberties are restricted for civic, medical, charitable or correctional purposes including:

(a)	Asylums

Hospitals

Infirmaries

Old and handicapped persons homes

Sanatoria

(b)	Prisons

Reformatories

301.4		Group C. Commercial and Industrial Buildings

Being buildings used for manufacture, assembly, servicing, repair and factory operations or for the storage except for display purposes of materials or finished products where no hazardous processes or materials are involved and including:

(a)	Aeroplane hangers

Cold storage buildings

Freight depots

Parking garages

Warehouses

(b)	Factories

Commercial laboratories

Laundries

Processing plants

Power stations

Telephone exchanges

Workshops

301.5		Group D. Office, Administrative and Retail Service Buildings

Being buildings used for business or professional transactions or the display or sale of materials or finished products and including:

(a)	Banks

Civic administration buildings

Radio stations

Restaurants seating less than 50 persons

Television stations

Office buildings

(b)	Markets, Supermarkets

Shops

Showrooms

Stores

301.6		Group E. Residential Buildings

Being all buildings in which sleeping accommodation is a necessary or major provision, except buildings classified under Group B in 301.3 of this Code and including:

(a)	Apartment buildings containing less than 10 apartments.

Guest houses accommodating less than 25 persons.

Private residences and duplex buildings.

Residential club accommodation for less than 25 persons.

Terrace houses.

(b)	Apartment buildings containing 10 or more apartments.

Guest houses accommodating 25 or more persons.

Halls of residence.

Hotels.

Motels.

Residential club accommodation for more than 25 persons.

(c)	Tenement buildings.

Dormitories.

301.7		Group F. Hazardous Occupancy Buildings

Being buildings or parts of buildings for the storage or handling or use or processing of any of the hazardous materials or for the housing or carrying out of any of the hazardous processes listed and attached to this Code as Appendix D, or buildings used for any other purpose which, in the opinion of the Authority, creates hazardous or noxious conditions.

302		OCCUPANCY CONTENT OF A BUILDING

302.1		Basis of Calculation

a)	Table 3-1 shall determine the number of persons occupying a building or part of a building subject to the special provisions of 306 of this Code, and except the building or part of the building be planned for a greater number persons than that determined from Table 3-1 then the greater number shall be used, and any enclosed space or room which 50 or more persons regularly congregate shall be considered a place of public assembly regardless of the group classification of the building.

b)	Appendix H provides information on the specific requirements of the Occupancy Groups. This appendix is included for guidance to designers. However Table 3-1 must be used to determine the minimum occupancy content of buildings. Designers of public buildings should apply to the Authority for permission to alter any of the minimum areas given in the Table 3-1, where there is mixed occupancy or doubt as to the appropriate area to be used.

Table 3-1

Occupancy Content of a Building

| Places of public assembly in any building | 1 person for each seat, (7 sq.ft required). For the occupancy content of other assembly buildings see Appendix H (1) Section 5. |
| --- | --- |
| Group A. Public buildings generally, Restaurants, night clubs | 1 person for each 100 sq.ft of floor area. 1 person for each 12 sq.ft. (net). |
| Group B. Institutional buildings generally Hospital surgical and obstetrical areas | Group B (b): 1 person for each 100 sq.ft of floor area. 1 person for each 120 sq.ft. of floor area. |
| Group B. Institutional buildings: open wards and dormitories | 1 person for each 50 sq.ft. of area. |
| Group C Commercial and industrial buildings | Group C (a): 1 person for each 200 sq.ft. of floor area for the first 5 persons and 1 person for each 1,000 sq.ft of floor area thereafter Group C (b): 1 person for each 50 sq.ft. of floor area for the first 10 persons. 1 person for each 100 sq.ft. of floor area for the next 10 persons, and 1 person for each 500 sq.ft. of floor area thereafter. |
| Group D. Offices, administrative and retail service buildings | Group D (a): 1 person for each 100 sq.ft of floor area Group D (b): 1 person for each 50 sq. ft of sales floor area plus 1 person for each 100 sq.ft. of non sales floor area. |
| Group E. Residential | Group E (a): 1 person for each 300 sq.ft of floor area Group E (b): 1 person for each 150 sq.ft. of floor area Group E (c): 1 person for each 50 sq.ft. of floor area. |
| Group F. Hazardous occupancy | 1 person for each 50 sq.ft. of floor area for the first 10 persons, 1 person for each 500 sq.ft. of floor area thereafter |

303		TYPE CLASSIFICATION BY CONSTRUCTION

303.1		General

a)	The requirements of Types of Construction in this Sub-section are minima for the various Types of Construction and are intended to represent varying degrees of public safety and resistance to fire. For the purpose of this Code, Type I shall be deemed to be the most fire-resistive and Type 5 the least fire-resistive Type of Construction.

b)	All buildings and structures shall be classified into one of the following Types of Construction:

Type I Buildings: 	Fire Resistive

Type 2 Buildings:	Semi-fire Resistive

Type 3 Buildings:	Ordinary Masonry (Protected and Unprotected)

Type 4 Buildings:	Noncombustible

Type 5 Buildings:	Wood Frame

Appendix I provides more information on the specific requirements for each Type.

c)	In order that a building or structure may be classified in any specific Type of Construction, it is necessary that all the requirements for that Type shall be at least equalled. No building or portion thereof shall be required to conform to the details of a Type of Construction higher than that Type for which the minimum requirements based on Occupancy are met even though certain features of such building actually conform to a higher Type of Construction.

d)	Where specific materials, Types of Construction or fire-resistive protection are required, such requirements shall be the minimum requirements, and any materials Types of Construction or fire-resistive protection which will afford equal or greater public safety or resistance to fire, as specified in this Code, may be used, subject to the requirements of Sub-sections 401 and 402 of this Code covering alternate materials and construction standards.

e)	Where two or more Types of Construction occur in the same building and are separated by firewalls as required in the Chapters of Occupancy, each portion so separated may be classified as of the Type of Construction to which it conforms. If firewalls are not provided as required in Sub-section 406.3, the whole building shall be classified as the least fire-resistive Type of Construction used and shall be subject to the restrictions imposed upon that Type.

f)	The structural frame shall be considered to be the columns and the girders, beams, trusses and spandrels having direct connections to the columns and all other members which are essential to the stability of the building as a whole. The members of floor or roof panels which have no connection to the columns shall be considered secondary members and not a part of the structural frame.

g)	Minor accessory buildings of unprotected non-combustible materials not exceeding 10 percent of the ground floor of the primary building, nor 1,500 square feet, whichever is larger, may subject to the specific approval of the Authority, where separated from the primary building as required in the Code, be constructed without changing the fire-resistive classification of the primary building based on Type of Construction.

303.2		Existing Buildings

An existing building which by its construction cannot be definitely classed as of Type I, 2, 3, 4 or 5 as defined in this Code shall be defined for the purpose of this Code, by the Authority.

303.3		Abbreviations

For the purpose of 303 and in interpretation of Table 3-2 the following abbreviations shall have the meanings given to them hereunder:

FRC		Fire resistance rated construction containing combustible materials

FRTW		Fire resistance rated and fire retardant treated wood

FRW		Fire resistance rated wood

N/A 		Not applicable

NFR		Fire resistance rated construction of non-combustible materials

NM		Non-combustible materials

PS		Fire resistance rated protected structural steel

RC 		Fire resistance rated reinforced concrete

TW 		Fire retardant treated wood

W 		Unrated untreated wood

303.4		Basis of Classification

Table 3-2 shall be used to establish Type classification by construction of a building subject to the special provisions of 306 of this Code and provided that where any building does not clearly fall into one of the five Types defined it shall be classified under the most restrictive of the Type it resembles.

304		PERMISSIBLE AREAS AND HEIGHTS

304.1		Abbreviations

For the purpose of 304 and in interpretation of Table 3-3 the following abbreviations shall have the meaning given them hereunder:

Group:	Group classification by use and occupancy under 301 of this Code

NL:	No limit

NP:	Not permitted

Type:	Type classification by construction under 303 of this Code.

SS:	Single storey

MS:	Multi-storey

304.2		Basis of Determination

Table 3-3 shall determine the maximum permitted area and height of a building subject to the special provisions of this Code  and provided that where two or more parts of a building are separated from one another by divisions satisfying the fire resistance requirements of this Code for the most restrictive use, then the maximum permitted areas may be applied to each part so divided.

305		FIRE RESISTANCE RATING FOR BUILDINGS

305.1		Basis of Determination

Tables 3-4 to 3-7 inclusive shall determine the minimum fire resistance ratings for the component parts of a building subject to the special provisions of 306 of this Code and provided that the permitted fire resistance ratings of various materials and combinations of materials shall be established in accordance with this Code.

306 		SPECIAL PROVISIONS

306.1		Interpretation

The requirements of 306 are to be read and interpreted with 301 to 305 of this Code provided that if the requirement of two or more sections should appear contradictory when applied to a particular building, the more restrictive requirements shall apply.

306.2		General Occupancy

(a)	Any building with an occupancy content of more than 1,000 persons as calculated from Table 3-1 shall be of Type 1 construction.

(b)	No building of Group A: Table 3-1 with an occupancy content of more than 250 persons as calculated from Table 3-1 shall be of Type 4 or 5 construction.

306.3		Hazardous Occupancy

(a)	Buildings used to store highly combustible or highly inflammable materials or liquids shall be of Type 1 or 2 construction, not more than 12' 0" in storey height, not closer than 50' 0" to a site boundary or to an adjacent  building on the same site and divided by fire division walls into separate parts, each part not exceeding 5,000 sq. ft. in floor area.

(b)	Buildings housing processes using combustible or inflammable liquids with a flash point lower than 190 degrees F shall be of Type 1 or 2 single storey construction not closer than 50' 0" to a site boundary or to an adjacent building on the same site and shall be separated by fire division walls into separate parts, each part not exceeding 10,000 sq.ft. in floor area.

306.4		Areas, Heights and Volumes

(a)	A building of Type 1 construction more than 100'-0" high may be required to have higher fire resistance rating for any or all of the component parts and the whole or any part of the building shall be equipped with wet and/or dry risers if required by the Director.  These risers and fittings shall be subjected to an acceptance test and be certified by the Director.

(b)	The permissible areas given in Table 3-3  may be increased by 25 percent for any building having clear access to public streets on two sides.

(c)	The permissible area given in Table 3-3 may be increased by 50 percent for any building having clear access to public streets on three or more sides.

(d)	The permissible areas given in Table 3-3 may increased by 100 percent for any multistorey building equipped with an approved automatic sprinkler system where such system is not specifically required by this Code.

(e)	The permissible areas given in Table 3-3 may be increased by 200 percent for any single storey building equipped with an approved automatic sprinkler system where such system is not specifically required by this Code.

(f)	Any building more than 250,000 cu.ft. in volume shall, unless equipped with an approved automatic sprinkler system be divided by fire division walls, fire division floors, and or ceilings, into parts not exceeding 250,000 cu.ft.in. volume.

306.5		Special Fire Resistance Ratings

(a)	In buildings of Groups A,C,D, and E, not more than 50'0" high and not closer than 50'0" to a site boundary or to an adjacent building on the same site, non-load-bearing exterior walls may be of non rated combustible materials.

(b)	Suspended ground floors with less than 3'0" clearance need not be of fire resistance rated construction for Groups A and E. For Types 1,2 and 4, construction shall be of non-combustible materials.

(c)	Roofs, where every part of the structural framework is more than 20'0" above the highest part of any floor, need not be of fire resistance rated construction, but for Groups A and F, and for Types 1,2 and 4 construction shall be of non-combustible materials.

(d)	Untreated wood or other combustible materials may be used only for wall and floor finishes, skirtings window sills, wall trims, staircase handrails and other minor non-structural decorative purposes.

NOTE: 	Untreated wood should not be used as wall finishes or handrails on escape routes.

Table 3-2

Type Classification by Construction

| Item | Type 1 Fire resistant | Type 2. Semi-fire resistant | Type 3. Ordinary Masonry | Type 4. Non-combustible | Type 5. Wood frame |
| --- | --- | --- | --- | --- | --- |
| Exterior structural | RC or PS | RC or PS | RC or PS | NFR, FRTW | NFR |
| Interior structural frame | RC or PS | RC or PS | NFR or FRTW | NM | NM or TW |
| Exterior load bearing walls | NFR | NFR | NFR | NFR | NFR or FRTW |
| Exterior non-load bearing walls | NFR | FRC or NFR | FRW | NFR | FRC or FRW |
| Interior load bearing walls | NFR | NFR | NFR or FRTW | NM | NM or FRW |
| Party walls and fire division walls | NFR | NFR | NFR | NFR | NFR or FRW |
| Interior walls enclosing vertical openings in buildings more than 1 storey high | NFR OR FRTW | NFR or FRTW | FRC or FRTW | NFR | FRC or FRW |
| Interior walls and/or doors facing on to a means of escape | NFR OR FRTW | NFR | FRC or FRTW | NFR or FRW | FRC or FRW |
| Fire division floors | NFR | NFR | NFR | NFR | NFR or FRW |
| Other floors | NFR | NFR OR FRTW | Group C: NFR or FRW Other Groups: NM OR TW | NM | NM or W |
| Roofs | NFR OR FRTW | NFR OR FRTW | NFR OR FRTW | NM | NFR OR FRTW |
| Cantilivered projections | NFT | NFR OR FRTW | NFR OR FRTW | NFR | NFR OR FRTW |

Note:	See 303.3 for abbreviations used

Table 3-3

Permissible Areas and Heights

| Group | Areas and Heights | Type 1. Fire resistant | Type 2. Semi-fire resistant | Type 3. Ordinary masonry | Type 4. Non-combustible | Type 5. Wood frame |
| --- | --- | --- | --- | --- | --- | --- |
| Group A | Area per storey | NL | 15,000 | 10,000 | 10,000 | 10,000 |
|  | Height (ft) | 100 | 60 | SS | SS | SS |
| Group B | Area per storey | NL | 10,000 | 7,500 | NP | NP |
|  | Height (ft) | 100 | 60 | 35 | NP | NP |
| Group C | Area per storey | NL | NL for SS 20,000 for MS | 15,000 | 15,000 | 10,000 |
|  | Height (ft) | 100 | 60 | 35 | SS | SS |
| Group D | Area per storey | NL | 20,000 | 15,000 | 15,000 | 10,000 |
|  | Height (ft) | 100 | 60 | 35 | SS | SS |
| 222222Group E | Area per storey | NL | 15,000 | 10,000 | 7,500 | 7,500 |
|  | Height (ft) | 100 | 60 | 35 | 25 | 25 |
| Group F | Area per storey | 15,000 | 10,000 | 7,500 | 5,000 | NP |
|  | Height (ft) | 60 | 25 | SS | SS | NP |

Note: Read this Table with 306 of this Code. For abbreviations used see 304.1

Table 3-4

Fire resistance ratings in hours for buildings within 10'0" of site boundaries or adjacent buildings on the same site

| Item | Type 1. Fire resistant | Type 2. Semi-fire resistant | Type 3. Ordinary Masonry | Type 4. Non-combustible | Type 5. Wood frame |
| --- | --- | --- | --- | --- | --- |
| Exterior structural frame | 4 | 3 | 2 | 2 | 1 |
| Interior structural frame | 3 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Exterior load bearing walls | 4 | 2 | 2 | 2 | 1 |
| Exterior non-load bearing walls | 3 | 2 | 2 | 1 | 1 |
| Interior load bearing walls | 2 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Party walls | 4 | 3 | 3 | 3 | 2 |
| Fire division walls | 3 | 2 | 2 | 2 | 1 |
| Interior walls enclosing vertical openings in buildings more than 1 storey high | 2 | 1 | 1 | 1 | 1 |
| Interior walls and/or doors facing on to means of escape | 1 | 1/2 | 1/2 | 1/2 | 1/2 |
| Interior walls not otherwise described | Groups A & D only: 1/2 | Groups A & D only: 1/2 | 0 | 0 | 0 |
| Fire division floors and/or ceilings | 3 | 2 | 2 | 2 | 1 |
| Other suspended floor and/or ceilings | 2 | 1 | 1 | 1 | 1 |
| Roofs | 2 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Cantilevered projections | 3 | 2 | 2 | 1 | 1 |
| Fire check doors | 1 | 1/2 | 1/2 | 1/2 | 1/2 |

Note: See 303.3 for abbreviations used

Table 3-5

Fire resistance rating in hours for buildings between 10'0" and 20'0" from

site boundaries or adjacent buildings on the same site.

| Item | Type 1. Fire resistant | Type 2. Semi-fire resistant | Type 3. Ordinary masonry | Type 4. Non-combustible | Type 5. Wood frame |
| --- | --- | --- | --- | --- | --- |
| Exterior structural frame | 3 | 2 | 1 | 1 | 1 |
| Interior structural frame | 2 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Exterior load bearing walls | 3 | 2 | 1 | 1 | 1 |
| Exterior non-load bearing walls | 2 | 1 | 1 | 1 | 1 |
| Interior load bearing walls | 2 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Fire division walls | 3 | 2 | 1 | 1 | 1 |
| Interior walls enclosing vertical opening in buildings more than 1 storey high | 2 | 1 | 1 | 1 | 1 |
| Interior walls facing on to means of escape | 1 | 1/2 | 1/2 | 1/2 | 1/2 |
| Interior walls not otherwise described | Groups A & D only: 1 | Groups A & D only: 1/2 | 0 | 0 | 0 |
| Fire division floors and/or ceilings | 3 | 2 | 1 | 1 | 1 |
| Other suspended floors and/or ceilings | 2 | 1 | 1 | 1 | 1 |
| Roofs | 2 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Cantilevered projections | 2 | 1 | 1 | 1 | 1 |
| Fire check doors | 1/2 | 1/2 | 1/2 | 1/2 | 1/2 |

Table 3-6

Fire resistance ratings in hours for buildings over 20'0" from site boundaries

or adjacent buildings on the same site and more than 35 '0" high.

| Item | Type 1. Fire resistant | Type 2. Semi-fire resistant | Type 3. Ordinary masonry | Type 4. Non-combustible | Type 5. Wood frame |
| --- | --- | --- | --- | --- | --- |
| Exterior structural frame | 2 | 2 | N/A | N/A | N/A |
| Interior structural frame | 2 | 1 | N/A | N/A | N/A |
| Exterior load bearing walls | 2 | 2 | N/A | N/A | N/A |
| Exterior non-load bearing walls | 2 | 1 | N/A | N/A | N/A |
| Interior load bearing bearing walls | 2 | 1 | N/A | N/A | N/A |
| Fire division walls | 2 | 2 | N/A | N/A | N/A |
| Interior walls enclosing vertical opening in buildings more than 1 storey high | 1 | 1 | N/A | N/A | N/A |
| Interior walls not otherwise described | Groups A & D only: 1/2 | Groups A & D only: 1/2 | N/A | N/A | N/A |
| Fire division floors and/or ceilings | 2 | 1 | N/A | N/A | N/A |
| Roofs | 2 | 1 | N/A | N/A | N/A |
| Fire check doors | 1/2 | 1/2 | N/A | N/A | N/A |

Table 3-7

Fire resistance ratings in hours for buildings over 20'0" from site boundaries

or adjacent buildings on the same site and up to 35' 0' high

| Item | Type 1. Fire resistant | Type 2. Semi-fire resistant | Type 3. Ordinary masonry | Type 4. Non-combustible | Type 5. Wood frame |
| --- | --- | --- | --- | --- | --- |
| Exterior structural frame | 2 | 1 | 1 | 1 | 1 |
| Interior structural frame | 1 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Fire division walls | 2 | 2 | 1 | 1 | 1 |
| Interior walls enclosing vertical openings in buildings more than 1 storey high | 1 | 1 | 1 | 1 | 1 |
| Interior walls facing on to a means of escape | 1/2 | 1/2 | 1/2 | 1/2 | 1/2 |
| Fire division floors and/or ceilings | 2 | 2 | 1 | 1 | 1 |
| Other suspended floors and/or ceilings | 1 | 1 | 1 | 1 | 1 |
| Roofs | 1 | 1 | 1 | SS: 1/2 MS: 1 | SS: 1/2 MS: 1 |
| Cantilevered projections | 1 | 1 | 0 | 0 | 0 |
| Fire check doors | 1/2 | 1/2 | 1/2 | 1/2 | 1/2 |